Looking back on 2001 Changes Energy Code.

Title 24-Data, LP

Frazier Park, CA.  93225-2199

Toll Free 800-237-8824

[e-mail]  title24@frazmtn.com

www.title24.qpg.com

Looking back on the year 2001, new, more stringent

California Energy Standards (AB970) came into effect.

Next will come the 2005 Standards I will discuss at a later date.

Air Conditioning Contractors, have you noticed the 25% tightening of the Non-Residential Standards.

What was the hurry for the California legislature to pass AB970.  Officials in the CEC a year earlier said that they were not going to change the Standards until 2005.  What happened to change that?

California, since the 1978 energy standards, has always been the leader in energy efficiency standards.

It wasn't the utility crunch that pushed California to rush New Standards into LAW.

It was the new ASHRAE Standard 90.1.  Standard 90.1 is a national Energy Standard for Buildings,  with the exception of Low Rise Residential Buildings.  This Standard is more stringent than California's energy requirements was.  That meant as states adopted the new standard they would be ahead of California and that just can’t be tolerated!

ASHRAE, (American Seociety of Heating, Refrigerating & Air-Conditioning Engineers) adopted 90.1 in June 1999.  This new more stringent efficiency standard is written in code language, not like a engineers handbook.  This allows fast adoption by the states.  More than half of the states already adopted the earlier version of 90.1 and are in a position to push this revision through their legislatures quickly.

We are now seeing the results 90.1 and AB970. They are going to cause a new era in construction requirements.

In your hand outs we have given you a quick summary of the changes in the new California Standards, both residential and non-residential.  We have also included 2 case studies.  Each case study is a 2000 square foot building, one residential and one non-res.  We have created a buildings that just barely complied under the previous standards.  We wanted you to see the effects the new Standards would have on the design of these 2 case studies.  We have calculated these buildings in 3 climate zones.   Zone 9, SF Valley.  Zone 6, Coastal.  Zone 14, Palmdale - Lancaster.

As you look over the changes in the Standards, what jumps out?  What is there that you see that you question?

1.  New requirements in the base building model for windows and skylights were set with lower U-factors and SHGC values means less glass or better windows.

2.  A “Cool Roof” compliance option is available.

3.  New Federal requirements for equipment efficiencies take effect 10/29/01.

4.  Demand ventilation controls are required for HVAC systems serving area identified in Chapter 10 UBC as assembly areas, concentrated use (without fixed seats), auction rooms, or have design outdoor air capacities equal to or exceeding 3000 cfm.  This means a CO2 sensor is needed.

5.  Portable lighting shall be included in the proposed lighting budget of the energy calculations for offices.   If no specific plans for  portable office lighting are provided, the standards specify a default value of 0.2 w/sq. ft. for the task lighting to be used to determine the actual lighting power density.

6.  Credit is given for  tight ducts on packaged system serving 5000 sq. ft. of conditioned floor area or less that is located between an insulated ceiling and the roof.  Ducts must be tested by third-party field verification and leakage cannot exceed  6%.   Additional credit an be achieved with higher R-value duct insulation.

Effective Dates:

	June 1, 2001    - 	All Non-residential projects permitting on or after this date must comply with the 2001 Standards which will save 20% of the energy use.

	October 29, 2001   - 	By  Federal law, all Space Conditioning Equipment built on or after this date must meet the new Federal efficiency standards.

New Terms:

	 The term “U-value” is now “U-Factor”.

Climate Zones:

	Climate zones have been regrouped to form groups with the same prescriptive envelope requirements.

Envelope Changes:

	New requirements for windows and skylights were set with lower U-factors and SHGC values.  Vertical glazing is dependant on the window-to-wall ratio.  Skylight values are dependant the type of skylight construction and percentage of glass.

	Certification and labeling of fenestration products will..to include site built products.  An exception is made for buildings less than 100,000 sq. ft. or less than 10,000 sq. ft. of glass.

	A “Cool Roof” compliance option is available.  Cool roofs use materials with higher solar reflectance properties (i.e. tile with reflectance of 0.40 or higher; others with reflectance of 0.70 or higher).   Cool roofs have better absorptivity values.

	Cool roof products  must meet the labeling and certification requirements relating to reflectance and emittance for roofing products effective January 1, 2003. Until this date, manufacturers’ published performance data shall be acceptable to show compliance.

Glazing Orientation Tables:

	Replaces previous data with individual values for each climate zone and provides different values for Non-residential and High-Rise Residential projects.

Exterior Lighting:

	Conditioned buildings that have exterior lighting which is attached to or powered by the electrical service in the building shall be controlled by a directional photocell or an astronomical time switch that is automatically turns off the exterior lighting when daylight is available.

Interior Lighting:

	Incandescent or tungsten-halogen luminaries with medium screw base sockets and not containing permanently installed ballasts shall be counted in the energy calculations at the maximum labeled wattage of the luminaire.

	Luminarie wattage (with permanently installed or remotely installed ballast)  shall be the operating input wattage of the specified lamp/ballast combination based on values from the manufacturer’s catalogs or values from independent testing lab reports.

	Line-voltage lighting track and plug-in busways which allows the addition or relocation of luminaries without altering the wiring of the system, shall be the volt-ampere rating of an integral current limiter controlling the luminaries OR, the HIGHER of the specified wattage of the luminaries included in the system or 45 watts per linear foot.

	“Exit” signs shall be included in the actual lighting power calculations excluding those with an input power rating of five (5) watts per illuminated face or less.

	Bi-level switching is now required for spaces over 100 sq. ft.  that have a lighting load greater than 0.8 w/sq. ft.   (Previously, this allowance was 1.0 w/ sq. ft.)

	Bi-level switching is exempt in corridors.

	Lumen Maintenance controls are no longer  a credit.

	The allowed lighting power has been reduced 6% - 13% for  convention centers, hotel lobbies and lock/dressing rooms.

Task					1998 ALP			2001 ALP

Convention, conference,

multi-purpose, meeting ctrs		1.6				1.5

Hotel Lobby					2.2				1.7

Locker/dressing Rms			0.9				0.8

	Portable lighting shall be included in the proposed lighting budget of the energy calculations for offices.  This type of lighting includes track and flexible lighting systems, lighting that is integral with modular furniture, workstation task lights, portable freestanding lights, lights attached to workstation panels, movable displays and cabinets, internally illuminated case work for task or display purposes.  These lights shall only be calculated  office occupancy allowed lighting power for spaces over 250 sq. ft.

	If no specific plans for  portable office lighting are provided, the standards specify a default value of 0.2 w/sq. ft. for the task lighting to be used to determine the actual lighting power density.

	Five (5) compliance options are available for portable office lighting power density (PLPD):

(1)  Default 0.2 w/ sq. ft.

(2) Actual PLPD

(3) PLPD provided by designer

(4) Non-Office Function or Office Function less than or equal to 250 sq. ft.

(5) Demonstrate adequate lighting levels are provided.

Mechanical Systems:

	New Federal requirements for equipment efficiencies take effect 10/29/01.

	Demand ventilation controls are required for HVAC systems serving area identified in Chapter 10 UBC as assembly areas, concentrated use (without fixed seats), auction rooms, or have design outdoor air capacities equal to or exceeding 3000 cfm.  This means a CO2 sensor is needed.

	Pipe insulation, Duct insulation, and insulation covering chilled water piping and refrigerant suction piping  shall be protected from damage, including that due to sunlight, moisture, equipment maintenance and wind.

	Acceptable high-limit shut-off control types for air-side economizers are specified based on climate zone such as Fixed Dry Bulb, Differential Dry Bulb, Fixed Enthalpy, Electronic Enthalpy, Differential Enthalpy.

Exception: There is an alternative to an economizer available in some specific climate zones and equipment size categories of electrically operated unitary air conditioners and heat pumps.

	Now there are requirements for heat rejection system controls.

	Fan Speed Control - each outdoor fan powered by a motor of  7.5 hp (5.6kW) or larger shall have the capability to operate that fan at two-thirds of full speed or less and shall have controls that automatically change the fan speed to control the leaving fluid temperature or condensing temperature/pressure of the heat rejection device.

	Credit is given for  tight ducts on packaged system serving 5000 sq. ft. of conditioned floor area or less that is located between an insulated ceiling and the roof.  Ducts must be tested by third-party field verification and leakage cannot exceed  6%.   Additional credit an be achieved with higher R-value duct insulation.

What is a HERS Rater?

"The California Energy Commission is required by Public Resources Code Section 25942 to establish regulations for a Home Energy Rating System (HERS) Program to certify home energy rating services in California. These services are to also include field verification and diagnostic testing available through Commission-certified providers and their raters when duct efficiency and envelope leakage measures are installed for complying with the new 1998 building efficiency standards (effective July 1, 1999). As of April 23, 2001 there are only 17 HERS raters listed for California and only three of these have rated a building.  That is scary!!  I am concerned about my clients.  In the cases where we model the credit of "tight ducts" or a "Thermostatic Expansion Valve, TXV" the designers who I work for are going to be at a loss to finish their jobs because there are no HERS raters to check out their job and with this great of a shortage they will raise their prices for this needed process of inspection and testing.

The goal of the program is to provide reliable information to differentiate the energy efficiency levels among California homes and to guide investment in cost-effective home energy efficiency measures. The notices and documents prepared by staff for the HERS rule-making are contained on the Commissions web site located at the following address:"

http://www.energy.ca.gov/HERS/index.html.

"The HERS program is intended to promote home energy efficiency, reduce energy utility bills and make housing more affordable in California, provide more comfortable and safe home environments, increase property values, and preserve California Environmental quality and energy security."

Where can I find a HERS Rater in California?

California Home Energy Efficiency Rating System
9400 Oakdale Avenue
Chatsworth, CA 91311
Phone: (818) 700-3600
Accreditation Identification Number: HERS 1999-027

Where can I find a HERS Rater in other states?

http://www.natresnet.org/accred/registry.htm