Residential Title 24 Changes for 2001

Title 24-Data, LP

Frazier Park, CA.  93225-2199

Toll Free 800-237-8824

[e-mail]  title24@frazmtn.com

www.title24.qpg.com

June 1, 2001	will be the first day new, more stringent California Energy Standards.

We hope you are ready for a 25% tightening of the Residential Standards.

With the Energy Crunch in California,  the legislature passed AB970 which mandated tighter energy standards.  The California Energy Commission produced extremely fast revisions.  We are seeing the results and they are going to cause a new era in construction requirements. What I wanted to discuss is the changes that HVAC contractors will most likely run into after June 1st.

Ducts:  heating and A/C ducts are now viewed as an extension of the building envelope.  Therefore more stringent duct installation will be expected.  Ducts must be sealed but to get credit for "tight ducts" on the energy calculations you must have the job inspected by a HERS Rater at a cost to the builder of $300+ per house inspected by them.

Tight ducts are part of the prescriptive package in all climate zones.  Using our Energy Budget Approach (mentioned above)  you may not be required to install them.  I feel they should be installed but if it is a requirement of your energy calculations you must have the job inspected by a HERS Rater.  This is costly in time and money at the end of the project, just when your client wants to move in.  The process is to have the HERS Rater appear on the job (much like a home inspector), remove all the registers and furnace access door than, using a special approved blower-pressure regulation,  pressurize the ducts and heating system and A/C coil.  The results must not be over 6% leakage.  When your test shows that your ducts leek over the 6% allowance, your heating man must return and find the leeks. Heating and A/C ducts are now viewed as an extension of the building envelope.  Therefore more stringent duct installation will be expected.  Ducts must be sealed, but to repeat the biggest issue I see,  to get credit for "tight ducts" on the energy calculations you must have the job inspected by a HERS Rater at a estimated cost to the builder of $300+ per house inspected by them.  The HERS Rater will fill out tightly controlled paperwork for the local jurisdiction and the State of California.

TXV:

Thermal Expansion Valve varies the flow of Freon to the A/C coil and is part of the Prescriptive Package.  If you take credit for this feature to save on A/C energy usage you will need to have the installation of the valve inspected by a HERS Rater just like the "tight ducts" feature above.

SEER ratings:

Using higher than the minimum 10.0 SEER used to get you a 20% reduction in cooling budget.  This has been changed to reflect reality, in some higher heat climates that 20% credit for going to a 12.0 SEER condenser has been reduced substantially.

Radiant Barrier:  will be expected, energy calculations will need this credit or have to get it some where else.  This barrier is part of the Prescriptive Packages in the hotter climate zones (2,4,8-15).  This foil is attached to the underside of the roof rafters from the attic and will reflect some heat back into space and is going to give you some compliance credit.

Windows:  We won't expect metal frames to comply easily.  High efficiency  windows, low SHGC and low "U" value in most California zones are going to be expected.  We won't expect metal frames to comply easily.  Why?  Dual glass metal frames have about the same energy "U" value as single glass non-metal (wood or vinyl).  I would advise to stay away from metal windows.  In areas where anodized metal is preferable why not use metal clad wood windows?

How do you do energy calculations on my project?

We expect most buildings will have to incorporate new conservation measures to comply with the new residential model.  Using our "Energy Budget Approach" (a computer modeling program)  your designed house is modeled against a model house based on your general conditions.  A energy budget for your designed house is produced.  This budget is the  model house with the CEC minimum "U" value windows, "R" value envelope insulation and HVAC/Water Heater efficiencies but with your floor area.   Next we model your designed house against that computer generated budget.  You will get credit for energy efficient features which are better than the model house and loose credit where your designs go beyond the allowance.  For example you might want more windows in your designed house than the 16% model house windows but have a more efficient water heater and furnace which would balance the energy losses of the oversized windows.  On the other hand,  you might substitute energy efficient windows to balance the loss created by going beyond the 16% budget.  You can see that this approach will allow flexibility for those view lots and custom homes that need more glass than 16% of the floor area budget.

Cost difference $$$:

Yes these changes will increase the cost of building homes.  Depending on the size of home, percent of windows, climate zone the bottom line figure ranges from several hundred to thousands of dollars.  The CEC contractors ran thousands of Micropas runs to determine alternative compliance strategies for each climate zone.  The goal was to find effective and practical measures to include in the Standards.  For each climate zone a number of solutions were identified, with projected costs.  In general two broad compliance options emerged:  either incorporate better fenestration products (low SHGC and low "U" value) or use a mix of improved HVAC products with field verification (tight ducts, TXV, ACCA duct design) and other related measures like Radiant Barriers or House Wraps.