Title 24-Data, LP

Frazier Park, Ca. 93225-2199

800-237-8824

Air Conditioning Contractors, How can you stay out of court?

We call it “forensic modeling”, that is,  reverse engineering a tract of homes,  a school and in one case a custom home.  My clients were  engineers hired by lawyers for the owners.  These lawyers were suing the developers,  general contractors and HVAC contractors just like you our readers.  They hired us to model the projects and report our findings on 1. Energy compliance issues, 2. Air conditioner/heater sizing & associated issues.

I write this for the benefit of architects, general contractors and mechanical contractors.  You want to avoid a law suits for improperly sized mechanical equipment.  I hope to mention some tips, things to avoid or watch for when comparing your energy audit or energy calculation equipment selection.  Many unqualified energy consultants are suggesting equipment that is oversized or undersized.  Unwary general contractors are installing the equipment assuming that the paperwork is correct and proper.  The equipment may be based on unreal conditions such as glass with a shade factor of .18 or with roller shades that are not used by the owners.  To elaborate;

1.  Glass was not installed that was calculated by the energy calculations, single instead of dual and worse yet metal frames where wood were on the energy calculations.  The heating & cooling loads were off by a large percent because of wrong windows!

2.  Condensers and furnaces installed were not as efficient as the energy calculations called for. (This will not effect the cooling/heating ability of the unit but does raise the utility bills.)

3.  The sensible load on the cooling calculations was used for the size of the condenser.  For example, in the San Fernando Valley a load calculation called for 3.5 tons sensible & the contractor installed a 3.5 ton condenser.  If he would have looked on the manufacture specification sheet for the condenser, he would have selected a 5 ton.  Why?  A 5 ton condenser at 100 degree design puts out 42000 BTU/Hour, a 3.5 ton output.  Be careful to use the specification sheets when selecting units.

4.  Check the cooling loads.  Did the energy consultant or engineer use shades or other coverings on the windows when doing the cooling loads?  If so, recalculate the solar gains using .88 SC or .77 SHGC as your factors for clear dual glass and add the difference to your total sensible before sizing your equipment. (You could call the author of the load calculations and have him do it for you.  It’s his error.)  This is a very common problem in the past, we see it all the time.  On a several phase development in Palm Springs we saw the mechanical equipment undersized by 50% on all the homes because the glass calculations used a .18 or 18% multiplier.  That is a 70% reduction in heat gain over what was actually installed!  (A housing tract in Pomona, Ca. will need $300,000 worth of upgrades because condensing units were undersized at least one ton on each house.  The energy consultant did the calculations correctly but selected the condensers based on roller shades pulled down all day.  The A/C contractor did not check the figures.)

5.  Sizing the equipment is the responsibility of the mechanical contractor unless there is a engineer signing the approved mechanical plans.  This is almost never done on residential projects.  So, do not accept the sizing of the energy consultant, double check the figures.  Most of them are not professionals, they are only documentation authors hired by the designer of the project!  The loads included with the energy calculations are a courtesy to you for your use.  You must select the equipment or verify the equipment selected because you are responsible!  You can not later fall back and ask for damages from the “Energy Analyst” because the designer counter signed his signature taking responsibility for the results.  You must sue the architect or designer.  He will than have to sue the “energy analyst” for damages due to his equipment selection.  It could be said during the lawsuit, the energy analyst’s selection was a guide but the Mechanical Contractor should have compared the loads to the equipment selection.

Proper equipment selection is quite involved.  In the design handbook from equipment manufacturer, let’s say you need 42,000 BTU/h sensible according to the cooling loads.  First you must choose:

1.  The entering wet bulb temperature; 2. The blower CFM; 3.  The outside design temperature, than find the unit that produces 42,000 BTU/h.  For mechanical contractors, your equipment supplier wants you to be successful.  Ask him where you might get better educated.

On many occasions, a trade publication, The Western HVACR News has allowed me to explain these issues in my column.  The effort is to encourage the unwary to learn as much as possible about their business.  If you are designing heating/A-C systems and do not know how to perform load calculations, you need someone who does.  What about night school?  Take air conditioning design classes.  Remember, education is better than litigation – and cheaper too!